| Connection tables | Version 1.0 | D |
| --- | --- | --- |
| Connection tables & connection variants Analyt / PoolManager® / PoolManager® PRO (5. generation „PoolManager 5“ / „PM5“) |
|  | Applicable for Analyt PoolManager® PoolManager® PRO |

- Relay switch outputs in the PoolManager® basic unit

| Name | Short name | Termi-nal | Function |
| --- | --- | --- | --- |
| Dosing Disinfection | Disinf. | [20] |  |
| Dosing pH Minus | pH- | [21] |  |
| Dosing pH Plus | pH+ | [22] |  |
| Alarm Relay(1) | Alarm | [25] |  |
| OUT1 | OUT1 | [26] |  |
| OUT2 | OUT2 | [27] |  |
| OUT3 | OUT3 | [30] |  |
| OUT4 - Working contact (n.o. normally open closes, if OUT4 switches ON) | OUT4-n.o. | [31] |  |
| OUT4 – Break contact (n.c. normally closed opens, if OUT4 switches ON) | OUT4-n.c. | [32] |  |

(1)	The alarm relay output can be released for alternative functions in the “Alarm settings” menu

Switch inputs in the PoolManager® basic unit

The PoolManager® has four universal switch inputs, to which external volts-free contacts or switches can be connected:

|  | IMPORTANT NOTICE! Volts-free contacts The connected external contacts or switches must absolutely be volts-free (dry contacts). In case of voltages on the external contact, the inputs of the PoolManager® or the external device may be destroyed. |
| --- | --- |

| Universal switch input | Description | Function |
| --- | --- | --- |
| IN 1 [6] | Switch input IN 1 [terminal 6] |  |
| IN 2 [7] | Switch input IN 2 [terminal 7] |  |
| IN 3 [8] | Switch input IN 3 [terminal 8] |  |
| IN 4 [9] | Switch input IN 4 [terminal 9] |  |

The following diagram shows the internal circuit of the switch input IN1.
The other inputs IN 2…IN 4 share the same circuit.

|  |  | 1 | Internal ground connection of the terminal b (the terminals b of all four switch inputs are internally connected to ground) |
| --- | --- | --- | --- |
|  |  | 2 | Optocoupler for galvanic isolation (internal) |
|  |  | 3 | Signal for further internal processing |
|  |  | 4 | Connected external volts-free contact or switch |

Temperature inputs in the PoolManager® basic unit

The PoolManager® has three temperature inputs for the connection of PT1000 type temperature sensors:

| Temperature input | Description | Function |
| --- | --- | --- |
| Temp.1 [3] | Temperature input 1 PT1000, 0-50°C | Pool temperature The standard PT1000 temperature sensor in the measuring chamber of the PoolManager® is connected here. For a better accuracy it may be replaced with a PT1000 sensor which is installed directly in the main circulation of the pool. |
| Temp.2 [4] | Temperature input 2 PT1000, 0-50°C |  |
| Temp.3 [5] | Temperature input 3 PT1000, 0-75°C |  |

Additional relay switch outputs
on the PM5-REL-4 plus (R4+) plug-in module

Order No. 127016 (optional)

| PM5-REL4 plus (R4+, new version) Up to three modules per controller RK(n.c.) = break contact (normally closed) AK(n.o.) = working contact (normally open) | PM5-REL4 (previous version) Only 1 module per controller Can be combined with up to 2 PM5-REL4 plus (R4+) modules. |
| --- | --- |

- First relay plug-in module (module A, left socket, PM5-REL4 plus or PM5-REL4)

| Name | Short name | Function |
| --- | --- | --- |
| OUT A1 (OUT5) – working contact (closes, if OUT A1 switches ON) | OUT A1-AK (n.o.) OUT5-AK (n.o.) |  |
| OUT A1 (OUT5) – break contact (opens, if OUT A1 switches ON) | OUT A1-RK (n.c.) OUT6-RK (n.c.) |  |
| OUT A2 (OUT6) – working contact (closes, if OUT A2 switches ON) | OUT A2-AK (n.o.) OUT5-AK (n.o.) |  |
| OUT A2 (OUT6) – break contact (opens, if OUT A2 switches ON) | OUT A2-RK (n.c.) OUT6-RK (n.c.) |  |
| OUTA3 (OUT7) | OUT A3 OUT7 |  |
| OUTA4 (OUT8) | OUT A34 OUT8 |  |

- Second relay plug-in module (module B, middle socket, PM5-REL4 plus)

| Name | Short name | Function |
| --- | --- | --- |
| OUT B1 – working contact (closes, if OUT B1 switches ON) | OUT B1-AK (n.o.) |  |
| OUT B1 – break contact (opens, if OUT B1 switches ON) | OUT B1-RK (n.c.) |  |
| OUT B2 – working contact (closes, if OUT B2 switches ON) | OUT B2-AK (n.o.) |  |
| OUT B2 – break contact (opens, if OUT B2 switches ON) | OUT B2-RK (n.c.) |  |
| OUT B3 | OUT B3 |  |
| OUT B4 | OUT B4 |  |

All switch outputs are volts-free and can switch the following
max. voltages and currents: 3A / 230V~ or 3A / 30V DC

- Third relay plug-in module (module C, right socket, PM5-REL4 plus)

| Name | Short name | Function |
| --- | --- | --- |
| OUT C1 – working contact (closes, if OUT C1 switches ON) | OUT C1-AK (n.o.) |  |
| OUT C1 – break contact (opens, if OUT C1 switches ON) | OUT C1-RK (n.c.) |  |
| OUT C2 – working contact (closes, if OUT C2 switches ON) | OUT C2-AK (n.o.) |  |
| OUT C2 – break contact (opens, if OUT C2 switches ON) | OUT C2-RK (n.c.) |  |
| OUT C3 | OUT C3 |  |
| OUT C4 | OUT C4 |  |

All switch outputs are volts-free and can switch the following
max. voltages and currents: 3A / 230V~ or 3A / 30V DC

Connection variant 1: Connection of the
internal 230V~ power supply of the PoolManager®

| 1 | External system to be controlled (to be switched ON or OFF) |
| --- | --- |
| 2 | Power supply 230V~ of the external system |
| 3 | Jumper from the phase LF (or LD) on the lowest terminal to the relay contact a on the middle terminal |

|  | Max. 4A in SUM for all outputs using this connection variant |
| --- | --- |

Connection variant 2:
Volts-free control signal

| 1 | External system to be controlled (to be switched ON or OFF) |
| --- | --- |
| 2 | Volts-free control input of the external system |

Max. 5A PER OUTPUT

Connection variant 3:
External 230V~ supply (from installation on site)

| 1 | External system to be controlled (to be switched ON or OFF) |
| --- | --- |
| 2 | Power supply 230V~ of the external system |
| 3 | External 230V~ supply (from the installation on-site) |
| 4 | External electrical protection (e.g. fuse) according to the local regulations |
| 5 | Switched phase L of the external 230V~ supply |

Max. 5A PER OUTPUT

Connection variant 4: External power switch
(230V~ or 400V~ contactor)

| 1 | External system to be controlled (to be switched ON or OFF) |
| --- | --- |
| 2 | Power supply 230V~ or 400V~ of the external system |
| 3 | Jumper from the phase LF (or LD) on the lowest terminal to the relay contact a on the middle terminal |
| 4 | Switched phase LF (or LD) for the contactor coil |
| 5 | External power switch (230V~ or 400V~ contactor) |
| 6 | External electrical protection (e.g. fuse) according to the local regulations |

Max. switching power is only limited by the external power switch (contactor)